Objectives

At the end of this introductory course, the student should be familiar with the following:

Reasons for carrying out flushing programs

Types of flushing programs

Various approaches to the setting up of a flushing program

Unidirectional flushing principles

Swabbing methods and applications to Ontario

Pigging, Water Blasting, and Hydro-Pneumatic Flushing (Air Scouring)

Safe Disposal of flushing and swabbing effluent

## Contents

## Introduction   8:00-8:15

# Why Flush or Swab ? 8:15 – 9:00

## Customer complaints-red water, black water, taste/odour, alginous   smell, air, turbidity

## Low residuals

#### HPCs

#### Biofilm development

## Dead ends-customer complaint/residual

## Lagoons-stagnation zones, complaints or model based

## Change in treatment chemistry-change in disinfection chemical, change in concentration, change in water supply chemistry

#### Lake Turnover Surface water-especially when unfiltered

## Loss of “C” factor

## Planned programs, compliance,

## Perception (Maggots, Crypto)

Types of flushing-Spot, conventional, automatic, unidirectional 9:30-9:45

BREAK   9:45-10:00

Some Flushing Science  10:00 – 10:30

The Reynolds experiments, as pertains to flushing, residual maintenance, etc

Exchange and Removal Approach

Calculation examples

Velocity Approach

Calculation examples

Blow offs, Bleeders and Automatic Flushers  10:30 –11:00

History, use and selection, hazards Continuous or intermittent

Size matters, minimum flows as per Reynolds number

Designed to change water over, not clean

Treats the symptom, not cause

Cons-cost, waste of water (non revenue water), Backflow possibility, dechlor issues, treatment of water

Maintenance

Hydro Guard, Kupferle, and shop made designs.

Flow rates and freeze protection

Costs

# Spot and Conventional \Flushing 11:00 – 11:15

## In conjunction with other maintenance

## Generally not organized or systematic

## Does not have lasting effect

## Quick and easy

## No special equipment

## Costs, risks, approaches

# Unidirectional Flushing  11:15-12:00

## Water flows in one direction only

## Method is systematic and pre-planned

## More effective scouring

## Uses less water in general

## Improved quality is longer lasting

# Principles of Unidirectional Flushing

## Work out from a source of clean water

## Break the system up into loops or paths (sequences)

## Work from large diameter to small diameter

## Close valves where necessary to ensure flow is from a clean source on a one way path

Ensure minimum flow rates to produce a flow velocity of 1.5 m/s in the largest diameter pipe segment

## Consider leaving completed areas partially isolated to prevent flow back from uncompleted areas (between flushing runs or sequences)

## Consider “normal” flow rates when setting flushing velocities / volumes

Don’t try to do too much at once

# Minimum Flows for Flushing Velocity

# Technical Requirements for Unidirectional Flushing

## Water map showing all valves, hydrants and water supplies

## Hydrant gate valves, discharge hose, flow diffusers, and tarps

## Valve keys and valve box flushers

## Pitot tube for measuring discharge rates

## Monitoring equipment (colourimeter, turbidimeter, pH meter, or white cup!)

## Filter bed trailer, sand bags, settling area, or sewer for discharge water

## Neutralizing agent for chlorine, chloramines, or pH

## Emergency phone numbers (Fire, Police and Environment)

# Record Keeping for Unidirectional Flushing

## Path ID number

## Number and ID of hydrants flowed

## Discharge rate, flushing time, and total volume

## Valves operated (times on and off)

## pH, chlorine residual, turbidity

# Record Keeping for Unidirectional Flushing

## Visual appearance of discharge / remarks

## Date, time, personnel

## Physical sample of discharge

## Lunch 12:00-12:30

## Swabbing  12:30-1:30

## More effective than unidirectional flushing (subject to water chemistry)

## Mechanical scrubbing of pipe wall

## More effective against slimes (PVC)

## Most lasting effects

## Comparatively low water usage

# Principles for Swabbing

## Work out from a source of clean water

## Work from large diameter to small diameter

## Close valves where necessary to ensure flow is from a clean source on a one way path

## Try to ensure 1 m/s flow speed

## Do test isolation first to ensure perimeter.

## Consider leaving completed areas partially isolated to prevent flow back from uncompleted areas between cleaning projects

#### Use blind seats, pressure relief valves.

## Consider swab condition when setting length of run.

## Avoid downhill runs

## Don’t try to do too much at once

# Technical Requirements for Swabbing

## Water map showing all valves, hydrants and water supplies

## Hydrant gate valves, discharge hose, flow diffusers, and tarps

## Valve keys and valve box flushers

## Swabs (1.5 lbs/cubic ft density)

## Monitoring equipment (colourimeter, turbidimeter, pH meter, or white cup!)

## Filter bed trailer, sand bags, settling area, or sewer for discharge water

## Neutralizing agent for chlorine, chloramines, or pH

## Emergency phone numbers (Fire, Police and Environment)

# Record Keeping for Swabbing

## Path ID number

## Discharge hydrant or blowoff ID

## Discharge rate, flushing time, number and  size of swabs

## Valves operated (times on and off)

## pH, chlorine residual, turbidity

## Visual appearance of discharge / remarks

## Condition of swabs/remarks

## Date, time, personnel

## Physical sample of discharge

# Risks of Unidirectional Flushing and Swabbing 1:30-2:00

## Broken valves

## Broken water main

## Negative pressures

## Exterior zone disruption / flow reversal

## Plugged services (swabbing)

## “Lost” swabs and techniques for locating

## Temporary difficulty maintaining residuals

## Break 2:00 –2:30

# Group Exercise (attached)   lay out a plan for swabbing or UDF, answering all questions and concerns on the question sheet

# Discuss answers and different approaches with other groups when complete  2:30-3:30

Brief discussion of other methods,  3:30-4:00

Air Scouring, Pigging, Water Blasting, Scraping

Costs, disadvantages, limitations.

4:00  Exam and review.